## Sheet1
No. | Name | Address | Data Type | Data Range | Unit | Note
1 | Reserved | 4950 - 4951 | U32
2 | Reserved | 4952 - 4953 | U32
3 | Reserved | 4954 - 4968 | U16
4 | Reserved | 4969 - 4983 | U16
5 | Reserved | 4984 - 4989 | U16
6 | SN | 4990 - 4999 | UTF-8 |  |  | Data type :UTF-8
7 | Device type code | 5000 | U16 |  |  | See Appendix 6
8 | Nominal Active Power | 5001 | U16 |  | 0.1kW
9 | Output type | 5002 | U16 | 0-two phase. 1-3P4L. 2-3P3L
10 | Daily power yields | 5003 | U16 |  | 0.1 kWh
11 | Total power yields | 5004 - 5005 | U32 |  | kWh
12 | Total running time | 5006 - 5007 | U32 |  | h
13 | Internal temperature | 5008 | S16 |  | 0.1℃
14 | Total Apparent Power | 5009 - 5010 | U32 |  | VA | Valid for inverters: SG5KTL-MT, SG6KTL-MT, SG8KTL-M, SG10KTL-M, SG10KTL-MT, SG12KTL-M, SG15KTL-M, SG17KTL-M, SG20KTL-M, SG3.0RT, SG4.0RT, SG5.0RT, SG6.0RT, SG7.0RT, SG8.0RT, SG10RT, SG12RT, SG15RT, SG17RT, SG20RT, SG33K3J, SG36KTL-M, SG40KTL-M, G50KTL, SG50KTL-M, SG60KTL, SG60KTL-M, SG60KU-M, G80KTL, SG80KTL-M, SG111HV, SG125HV, SG125HV-20, SG33CX, SG40CX, SG50CX, SG110CX, SG250HX, SG30CX, SG36CX-US, SG60CX-US, SG250HX-US, SG250HX-IN, SG25CX-SA, SG100CX、SG75CX, SG225HX
15 | MPPT 1 voltage | 5011 | U16 |  | 0.1V | See Appendix 6
16 | MPPT 1 current | 5012 | U16 |  | 0.1A | See Appendix 6
17 | MPPT 2 voltage | 5013 | U16 |  | 0.1V | See Appendix 6
18 | MPPT 2 current | 5014 | U16 |  | 0.1A | See Appendix 6
19 | MPPT 3 voltage | 5015 | U16 |  | 0.1A | See Appendix 6
20 | MPPT 3 current | 5016 | U16 |  | 0.1A | See Appendix 6
21 | Total DC power | 5017 - 5018 | U32 |  | W | See Appendix 6
22 | A-B line voltage/phase A voltage | 5019 | U16 | 0.1 V |  | Output type (address: 5002) is 1: upload phase voltage. 2: upload line voltage
23 | B-C line Voltage/phase B Voltage | 5020 | U16 |  | 0.1 V | Output type (address: 5002) is 1: upload phase voltage. 2: upload line voltage
24 | C-A line Voltage/phase C Voltage | 5021 | U16 |  | 0.1 V | Output type (address: 5002) is 1: upload phase voltage. 2: upload line voltage
25 | Phase A current | 5022 | U16 |  | 0.1 A
26 | Phase B current | 5023 | U16 |  | 0.1 A
27 | Phase C current | 5024 | U16 |  | 0.1 A
28 | Reserved | 5025 - 5026 | U32
29 | Reserved | 5027 - 5028 | U32
30 | Reserved | U32 | 5029 - 5030
31 | Total active power | 5031 - 5032 | U32 |  | W
32 | Total reactive power | 5033 - 5034 | S32 |  | Var
33 | Power factor | 5035 | S16 |  | 0.001 | >0 means leading. <0 means lagging
34 | Grid frequency | 5036 | U16 |  | 0.1 Hz
35 | Reserved | 5037 | U16
36 | Work state | 5038 | U16 | See Appendix 1 |  | Data of address 5039 - 5045 are additional
36 | Fault/Alarm time: Year | 5039 | U16 |  |  | Fault/Alarm time and Fault/Alarm code (5039 - 5045) are valid only when the device work state is fault (0x5500) or alarm (0x9100).
36 | Fault/Alarm time: Month | 5040 | U16 |  |  | Fault/Alarm time and Fault/Alarm code (5039 - 5045) are valid only when the device work state is fault (0x5500) or alarm (0x9100).
36 | Fault/Alarm time: Day | 5041 | U16 |  |  | Fault/Alarm time and Fault/Alarm code (5039 - 5045) are valid only when the device work state is fault (0x5500) or alarm (0x9100).
36 | Fault/Alarm time: Hour | 5042 | U16 |  |  | Fault/Alarm time and Fault/Alarm code (5039 - 5045) are valid only when the device work state is fault (0x5500) or alarm (0x9100).
36 | Fault/Alarm time: Minute | 5043 | U16 |  |  | Fault/Alarm time and Fault/Alarm code (5039 - 5045) are valid only when the device work state is fault (0x5500) or alarm (0x9100).
36 | Fault/Alarm time: Second | 5044 | U16 |  |  | Fault/Alarm time and Fault/Alarm code (5039 - 5045) are valid only when the device work state is fault (0x5500) or alarm (0x9100).
36 | Fault/Alarm code 1 | 5045 | U16 | See Appendix 3 |  | Fault/Alarm time and Fault/Alarm code (5039 - 5045) are valid only when the device work state is fault (0x5500) or alarm (0x9100).
36 | Reserved | 5046 - 5048 | U16
37 | Nominal Reactive Power | 5049 | U16 |  | 0.1kVar
38 | Reserved | 5050 - 5070 | U32
39 | Array insulation Resistance | 5071 | U16 | 1 - 20000(0xFFFF: invalid) | 1kΩ
40 | Reserved | 5072 | U16
41 | Reserved | 5073-5076
42 | Active Power Regulation Setpoint | 5077 - 5078 | U32 |  | 1w
43 | Reactive Power Regulation Setpoint | 5079 - 5080 | S32 |  | 1Var
44 | Work State | 5081 - 5082 | U32 |  |  | See Appendix 2
45 | Meter power | 5083 - 5084 | S32 |  | 1w | Valid for inverters: SG5KTL-MT, SG6KTL-MT, SG8KTL-M, SG10KTL-M, SG10KTL-MT, SG12KTL-M, SG15KTL-M, SG17KTL-M, SG20KTL-M. Note: Country set to Europe Area.
46 | Meter A phase power | 5085 - 5086 | S32 |  | 1w | Valid for inverters: SG5KTL-MT, SG6KTL-MT, SG8KTL-M, SG10KTL-M, SG10KTL-MT, SG12KTL-M, SG15KTL-M, SG17KTL-M, SG20KTL-M. Note: Country set to Europe Area.
47 | Meter B phase power | 5087 - 5088 | S32 |  | 1w | Valid for inverters: SG5KTL-MT, SG6KTL-MT, SG8KTL-M, SG10KTL-M, SG10KTL-MT, SG12KTL-M, SG15KTL-M, SG17KTL-M, SG20KTL-M. Note: Country set to Europe Area.
48 | Meter C Phase Power | 5089 - 5090 | S32 |  | 1w | Valid for inverters: SG5KTL-MT, SG6KTL-MT, SG8KTL-M, SG10KTL-M, SG10KTL-MT, SG12KTL-M, SG15KTL-M, SG17KTL-M, SG20KTL-M. Note: Country set to Europe Area.
49 | Load power | 5091 - 5092 | S32 |  | 1w | Valid for inverters: SG5KTL-MT, SG6KTL-MT, SG8KTL-M, SG10KTL-M, SG10KTL-MT, SG12KTL-M, SG15KTL-M, SG17KTL-M, SG20KTL-M. Note: Country set to Europe Area.
50 | Daily export energy | 5093 - 5094 | U32 |  | 0.1kWh | Valid for inverters: SG5KTL-MT, SG6KTL-MT, SG8KTL-M, SG10KTL-M, SG10KTL-MT, SG12KTL-M, SG15KTL-M, SG17KTL-M, SG20KTL-M. Note: Country set to Europe Area.
51 | Total export energy | 5095 - 5096 | U32 |  | 0.1kWh | Valid for inverters: SG5KTL-MT, SG6KTL-MT, SG8KTL-M, SG10KTL-M, SG10KTL-MT, SG12KTL-M, SG15KTL-M, SG17KTL-M, SG20KTL-M. Note: Country set to Europe Area.
52 | Daily import energy | 5097 - 5098 | U32 |  | 0.1kWh | Valid for inverters: SG5KTL-MT, SG6KTL-MT, SG8KTL-M, SG10KTL-M, SG10KTL-MT, SG12KTL-M, SG15KTL-M, SG17KTL-M, SG20KTL-M. Note: Country set to Europe Area.
53 | Total Import Energy | 5099 - 5100 | U32 |  | 0.1kWh | Valid for inverters: SG5KTL-MT, SG6KTL-MT, SG8KTL-M, SG10KTL-M, SG10KTL-MT, SG12KTL-M, SG15KTL-M, SG17KTL-M, SG20KTL-M. Note: Country set to Europe Area.
54 | Daily Direct Energy Consumption | 5101 - 5102 | U32 |  | 0.1kWh | Valid for inverters: SG5KTL-MT, SG6KTL-MT, SG8KTL-M, SG10KTL-M, SG10KTL-MT, SG12KTL-M, SG15KTL-M, SG17KTL-M, SG20KTL-M. Note: Country set to Europe Area.
55 | Total Direct Energy Consumption | 5103 - 5104 | U32 |  | 0.1kWh | Valid for inverters: SG5KTL-MT, SG6KTL-MT, SG8KTL-M, SG10KTL-M, SG10KTL-MT, SG12KTL-M, SG15KTL-M, SG17KTL-M, SG20KTL-M. Note: Country set to Europe Area.
56 | Reserved
57 | Daily running time | 5113 | U16 |  | 1min
58 | Present Country | 5114 | U16 |  |  | See Appendix 4
59 | MPPT 4 Voltage | 5115 | U16 |  | 0.1V | See Appendix 6
60 | MPPT 4 current | 5116 | U16 |  | 0.1A | See Appendix 6
61 | MPPT 5 voltage | 5117 | U16 |  | 0.1V | See Appendix 6
62 | MPPT 5 current | 5118 | U16 |  | 0.1A | See Appendix 6
63 | MPPT 6 voltage | 5119 | U16 |  | 0.1V | See Appendix 6
64 | MPPT 6 current | 5120 | U16 |  | 0.1A | See Appendix 6
65 | MPPT 7 voltage | 5121 | U16 |  | 0.1V | See Appendix 6
66 | MPPT 7 current | 5122 | U16 |  | 0.1A | See Appendix 6
67 | MPPT 8 voltage | 5123 | U16 |  | 0.1V | See Appendix 6
68 | MPPT 8 current | 5124 | U16 |  | 0.1A | See Appendix 6
69 | Reserved | 5125
70 | Reserved | 5126 - 5127
71 | Monthly Power Yields | 5128 - 5129 | U32 |  | 0.1kWh
72 | MPPT 9 voltage | 5130 | U16 |  | 0.1V | See Appendix 6
73 | MPPT 9 current | 5131 | U16 |  | 0.1A | See Appendix 6
74 | MPPT 10 voltage | 5132 | U16 |  | 0.1V | See Appendix 6
75 | MPPT 10 current | 5133 | U16 |  | 0.1A | See Appendix 6
76 | MPPT 11 voltage | 5134 | U16 |  | 0.1V | See Appendix 6
77 | MPPT 11 current | 5135 | U16 |  | 0.1A | See Appendix 6
78 | MPPT 12 voltage | 5136 | U16 |  | 0.1V | See Appendix 6
79 | MPPT 12 current | 5137 | U16 |  | 0.1A | See Appendix 6
80 | Reserved | 5138 - 5139 | U16
81 | Reserved | 5140
82 | Reserved | 5141
83 | Reserved | 5142
84 | Reserved | 5143
85 | Total Power Yields | 5144 - 5145 | U32 |  | 0.1kWh | (Display accuracy increased to 0.1kWh) Valid for inverters: SG5KTL-MT, SG6KTL-MT, SG8KTL-M, SG10KTL-M, SG10KTL-MT, SG12KTL-M, SG15KTL-M, SG17KTL-M, G20KTL-M, SG3.0RT, SG4.0RT, SG5.0RT, SG6.0RT, SG7.0RT, SG8.0RT, SG10RT, SG12RT, SG15RT, SG17RT, SG20RT, SG80KTL-M, SG111HV, SG125HV, SG125HV-20, SG33CX, SG40CX, SG50CX, SG110CX, SG250HX, SG30CX, SG36CX-US, SG60CX-US, SG250HX-US, SG250HX-IN, SG25CX-SA, SG100CX, SG75CX, SG225HX
86 | Negative voltage to the ground | 5146 | S16 | -15000 ~ 15000 | 0.1V
87 | Bus voltage | 5147 | U16 | 0 - 15000 | 0.1V
88 | Grid frequency | 5148 | U16 |  | 0.01Hz | (Display accuracy increased to 0.01Hz). Valid for inverters: SG5KTL-MT, SG6KTL-MT, SG8KTL-M, SG10KTL-M, SG10KTL-MT, SG12KTL-M, SG15KTL-M, SG17KTL-M, SG20KTL-M, SG3.0RT, SG4.0RT, SG5.0RT, SG6.0RT, SG7.0RT, SG8.0RT, SG10RT, SG12RT, SG15RT, SG17RT, SG20RT, SG80KTL-M, SG111HV, SG125HV, SG125HV-20, SG33CX, SG40CX, SG50CX, SG110CX, SG250HX, SG30CX, SG36CX-US, SG60CX-US, SG250HX-US, SG250HX-IN, SG25CX-SA, SG100CX, SG75CX, SG225HX
89 | Reserved | 5149 | U16 | 0 ~ 15000 | 0.1V
90 | PID work state | 5150 | U16 | 2: PID Recover Operation, 4: Anti-PID Operation, 8: PID Abnormity |  | Valid for inverters: SG5KTL-MT, SG6KTL-MT, SG8KTL-M, SG10KTL-M, SG10KTL-MT, SG12KTL-M, SG15KTL-M, SG17KTL-M, SG20KTL-M, SG3.0RT, SG4.0RT, SG5.0RT, SG6.0RT, SG7.0RT, SG8.0RT, SG10RT, SG12RT, SG15RT, SG17RT, SG20R, SG80KTL-M, SG125HV, SG125HV-20, SG80KTL, SG33CXSG40CX, SG50CX, SG110CX, SG100CX、SG75CX, SG136TX, SG250HX, SG30CX, SG36CX-US, SG60CX-US, SG250HX-US, SG250HX-IN, SG25CX-SA, SG225HX
91 | PID alarm code | 5151 | U16 | 432:PID resistance abnormal, 433:PID function abnormal, 434:PID overvoltage/overcur rent protection |  | See Appendix 5
92 | Reserved | 5152 | U16
93 | Reserved | 5153 - 7012